## Table 3-1
Application for an Energy Project Certificate and An Energy Operation Certificate Regarding The Proposed Whitehorse Diesel-Natural Gas Conversion Project | Yukon Energy Corporation UCG-YEC-1-2 Attachment 1 February 27, 2014
Table 3-1: Estimated Capital Costs for Initial Project Facilities at WTGS (2013 $Millions)
Activity | Estimated Costs ($million) | % Total Costs
Planning Costs | 2.4 | 6.983%
Engineering Services | 1.51 | 4.393%
Project Management | 1.03 | 2.997%
LNG Storage - EPC Contract | 4.57 | 13.3%
LNG - Site Development | 5.46 | 15.89%
LNG Gen - Engines | 11.44 | 33.28%
Grid Connection | 2.53 | 7.361%
Owners Costs - Construction Phase | 3.67 | 10.68%
BOP - Preliminary Assessment | 0.31 | 0.9019%
BOP - Decommissioning | 1.45 | 4.219%
Total | 34.37 | 100%

## Table 4-1
Application for an Energy Project Certificate and An Energy Operation Certificate Regarding The Proposed Whitehorse Diesel-Natural Gas Conversion Project |  |  |  | Yukon Energy Corporation UCG-YEC-1-2 Attachment 1 February 27, 2014
Table 4-1: Forecast Base Case (No Alexco) Grid Default Diesel Generation Requirement (2013-2030)
Year | 2013 | 2015 | 2020 | 2025 | 2030
Default Diesel Generation1 | 11 GW.h | 17 GW.h | 41 GW.h | 47 GW.h | 92 GW.h
1. Default diesel requirement based on long-term average hydro and wind generation, prior to development of any new nondiesel generation supply capacity on the grid (beyond what is permitted in 2013).

## Table 4-2
Application for an Energy Project Certificate and An Energy Operation Certificate Regarding The Proposed Whitehorse Diesel-Natural Gas Conversion Project |  |  | Yukon Energy Corporation UCG-YEC-1-2 Attachment 1 February 27, 2014
Table 4-2: Forecast Base Case (No Alexco) New Grid Capacity Requirement (2015-2030)
Year | 2015 | 2020 | 2025 | 2030
Forecast Non-Industrial Peak1 | 76.5 | 83.9 | 93.3 | 105.5
Reliable Capacity Required2 | 113.5 | 120.9 | 130.3 | 142.5
Existing Peak Winter Capacity3 | 106.5 | 100.2 | 84.7 | 78.9
New Capacity Requirement4 | 7 | 20.7 | 45.6 | 63.6
1. Non-industrial peak load on grid, after assumed Demand Side Management (DSM), less 1 MW for assumed Haines Junction load. See Appendix C.
2. Capacity planning requirements with N-1 reserve capacity (Forecast Non-Industrial Peak plus 37 MW for Aishihik hydro generation capacity [N-1 event is loss of transmission to the Aishihik hydro generation - also means loss of Haines Junction diesel capacity]).
3. Existing winter capacity in 2013 is 114.49 MW excluding Fish Lake hydro and Haines Junction diesel (see Table 2-3, Yukon Energy 20-Year Resource Plan: 2011-2030, December 2011). Reductions after 2013 reflect planned retirements of diesel engine units and the de-rated capacities of these units at this time (e.g., Mirrlees WD1 and WD2 have de-rated capacity of 8 MW versus rated capacity of 9.07 MW).
4. New capacity requirement equals forecast peak with N-1 reserve less existing peak winter capacity.

## Table 4-3
Application for an Energy Project Certificate and An Energy Operation Certificate Regarding The Proposed Whitehorse Diesel-Natural Gas Conversion Project |  |  |  |  | Yukon Energy Corporation UCG-YEC-1-2 Attachment 1 February 27, 2014
Table 4-3: Ratepayer Impacts from Whitehorse Diesel-Natural Gas Conversion Project ($million) (Project compared to New Diesel Alternative)
|  | 2014 | 2015 | 2016 | 2017 | 2018
Capital cost ($million) at yr end
Total | Diesel (new) | 22.545 | 11.1
| LNG | 34.36 |  | 4.4
Net | Diesel (new) | 22.545 | 33.1176 | 32.3128 | 31.5079 | 30.703
| LNG | 34.36 | 33.5373 | 37.1145 | 36.1818 | 35.249
Annual Capital Cost ($million)
Deprec | Diesel (new) |  | 0.52738 | 0.80488 | 0.80488 | 0.80488
| LNG |  | 0.82275 | 0.82275 | 0.93275 | 0.93275
Return | Diesel (new) |  | 1.5168 | 1.783 | 1.7391 | 1.6952
| LNG |  | 1.8502 | 1.9253 | 1.9973 | 1.9465
Total | Diesel (new) |  | 2.0442 | 2.5879 | 2.544 | 2.5001
| LNG |  | 2.673 | 2.748 | 2.9301 | 2.8792
Difference (LNG-Diesel) |  |  | 0.62877 | 0.16016 | 0.38609 | 0.37912
Annual Fuel Cost ($million)
Forecast Diesel (GWh) |  |  | 17 | 22.9 | 26.9 | 31.4
% New | Diesel (new) |  | 90% | 100% | 100% | 100%
| LNG |  | 100% | 95% | 100% | 100%
Fuel Cost | Diesel (new) |  | 4.2517 | 5.6334 | 6.6174 | 7.7244
| LNG |  | 2.295 | 3.2655 | 3.6315 | 4.239
Difference (LNG-Diesel) |  |  | -1.9567 | -2.3679 | -2.9859 | -3.4854
Net Ratepayer Impact ($million)
| Diesel (new) |  | 6.2959 | 8.2213 | 9.1614 | 10.2245
| LNG |  | 4.968 | 6.0136 | 6.5616 | 7.1182
Difference (LNG-Diesel) |  |  | -1.3279 | -2.2077 | -2.5998 | -3.1063
Notes:
1. All capital costs depreciated over 40 years; return on mid-year rate base at 5.45%/year.
2. Diesel fuel costs at 24.6 c/kWh new diesel, 28.7 c/kWh other diesel.
3. LNG delivered fuel costs at 13.5 c/kWh (assumes supply from Shell Canada at Calgary at an AECO gas price of $4.50 per MMBtu and using A-Train units for delivery to Whitehorse).

## Table 4-4
Application for an Energy Project Certificate and An Energy Operation Certificate Regarding The Proposed Whitehorse Diesel-Natural Gas Conversion Project |  |  |  |  | Yukon Energy Corporation UCG-YEC-1-2 Attachment 1 February 27, 2014
Table 4-4: Range of Capital Cost Increases Examined
Capital Cost Sensitivity: 13.1 MW LNG versus New Diesel ($million)
Added LNG Cost over Table 4-3
|  | Table 4-3 | 5% | 10% | 15% | 20%
| Diesel1 | 32.75 | 32.75 | 32.75 | 32.75 | 32.75
| LNG | 38.76 | 40.698 | 42.636 | 44.574 | 46.512
| Penalty | 6.01 | 7.948 | 9.886 | 11.824 | 13.762
| Annual | 0.4737 | 0.62645 | 0.7792 | 0.93195 | 1.0847
Maximum Annual Cost Penalty assumes 40 yr depreciation, Year 1 return at 5.45%
1. Diesel capital cost assumes $2.5 million per MW for 13.1 MW (Table 4-3 estimates $33.6 million capital cost for 13.4 MW, or $2.5 million per MW).

## Table 4-5
Application for an Energy Project Certificate and An Energy Operation Certificate Regarding The Proposed Whitehorse Diesel-Natural Gas Conversion Project |  |  |  | Yukon Energy Corporation UCG-YEC-1-2 Attachment 1 February 27, 2014
Table 4-5: Range of LNG Fuel Cost Savings Examined
LNG Fuel Cost Saving ($/kW.h)
| New Diesel | LNG |  |  | LNG Saving
A-Train from Calgary with 18% premium
| 0.246 | 0.115 | gas at $3.5/MMBTu, efficiency 44% |  | 0.131
| 0.2 | 0.115 | gas at $3.5/MMBTu, efficiency 44% |  | 0.085
| 0.246 | 0.135 | gas at $4.5/MMBTu, efficiency 40% |  | 0.111
| 0.2 | 0.135 | gas at $4.5/MMBTu, efficiency 40% |  | 0.065
Tridem from Calgary with 10% premium
| 0.246 | 0.133 | gas at $3.5/MMBTu, efficiency 44% |  | 0.113
| 0.2 | 0.133 | gas at $3.5/MMBTu, efficiency 44% |  | 0.067
| 0.246 | 0.154 | gas at $4.5/MMBTu, efficiency 40% |  | 0.092
| 0.2 | 0.154 | gas at $4.5/MMBTu, efficiency 40% |  | 0.046

## Table 4-6; Figure 4-1
Application for an Energy Project Certificate and An Energy Operation Certificate Regarding The Proposed Whitehorse Diesel-Natural Gas Conversion Project |  |  |  |  | Yukon Energy Corporation UCG-YEC-1-2 Attachment 1 February 27, 2014
Table 4-6: Ratepayer Cost Savings Sensitivity to Project Capital Costs and Fuel Cost Saving Risks
Maximum Annual LNG Capital Cost Penalty at 13.1 MW ($million/yr)1
|  | 0.4737 | 0.62645 | 0.7792 | 0.93195 | 1.0847
|  | Table 4-3 | plus 5% | plus 10% | plus 15% | plus 20%
LNG Fuel Cost Saving2
($/kW.h) |  | (Minimum LTA Displaced Diesel [GW.H/yr] to Break Even)
0.13 |  | 3.6439 | 4.8189 | 5.9939 | 7.1689 | 8.3439
0.11 | Table 4-3 | 4.3064 | 5.695 | 7.0837 | 8.4723 | 9.8609 |  | 0.11
0.09 |  | 5.2633 | 6.9606 | 8.6578 | 10.355 | 12.0523 |  | -0.02
0.07 |  | 6.7672 | 8.9493 | 11.1315 | 13.3136 | 15.4958 |  | -0.04
0.05 |  | 9.474 | 12.529 | 15.584 | 18.6391 | 21.6941 |  | -0.06
Notes: | 1. See Table 4-4 on Capital Cost Sensitivity
2. See Table 4-5 on LNG Fuel Cost Saving
3. 17 GWh LTA diesel forecast in 2015 with Base Case loads (no Alexco)
Application for an Energy Project Certificate and An Energy Operation Certificate Regarding The Proposed Whitehorse Diesel-Natural Gas Conversion Project | [6 empty] | Yukon Energy Corporation UCG-YEC-1-2 Attachment 1 February 27, 2014
Figure 4-1: Capital Cost & LNG Fuel Cost Savings Sensitivity

## Figure 3-1
Application for an Energy Project Certificate and An Energy Operation Certificate Regarding The Proposed Whitehorse Diesel-Natural Gas Conversion Project | [5 empty] | Yukon Energy Corporation UCG-YEC-1-2 Attachment 1 February 27, 2014
Figure 3-1: Annual Ratepayer Costs - LNG vs New Diesel: 2015-2018
Annual Ratepayer Cost for Capital & Fuel ($million per year)
|  | 2015 | 2016 | 2017 | 2018
| Diesel (New) | 6.2959 | 8.2213 | 9.1614 | 10.2245
| Gas/LNG | 4.968 | 6.0136 | 6.5616 | 7.1182
| Saving (Diesel-LNG) | 1.3279 | 2.2077 | 2.5998 | 3.1063

## Table C-1
Application for an Energy Project Certificate and An Energy Operation Certificate Regarding The Proposed Whitehorse Diesel-Natural Gas Conversion Project | [10 empty] | Yukon Energy Corporation UCG-YEC-1-2 Attachment 1 February 27, 2014
Table C-1: Updated Grid Load Scenarios
Forecast Years | Base Case no Alexco |  |  | Base Case with Alexco |  |  | Scenario A1 - Base Case w Carmacks Copper (no Alexco) |  |  | Scenario A2 - Base Case w Carmacks Copper (with Alexco) |  |  | Non-Industrial DSM/SSE (GW.h)
| Non-industrial Load (GW.h) | Industrial Load (GW.h) | Total Generation (GW.h) | Non-industrial Load (GW.h) | Industrial Load (GW.h) | Total Generation (GW.h) | Non-industrial Load (GW.h) | Industrial Load (GW.h) | Total Generation (GW.h) | Non-industrial Load (GW.h) | Industrial Load (GW.h) | Total Generation (GW.h)
2013 | 369.8507 | 43.5485 | 413.3991 | 369.8507 | 43.5485 | 413.3991 | 369.8507 | 43.5485 | 413.3991 | 369.8507 | 43.5485 | 413.3991 | 0
2014 | 377.9499 | 38.045 | 415.9949 | 377.9499 | 38.045 | 415.9949 | 377.9499 | 38.045 | 415.9949 | 377.9499 | 38.045 | 415.9949 | 0
2015 | 386.0609 | 40.219 | 426.2799 | 386.0609 | 55.437 | 441.4979 | 386.0609 | 40.219 | 426.2799 | 386.0609 | 55.437 | 441.4979 | 0.64437
2016 | 393.8652 | 43.48 | 437.3452 | 393.8652 | 60.872 | 454.7372 | 393.8652 | 43.48 | 437.3452 | 393.8652 | 60.872 | 454.7372 | 2.5264
2017 | 400.867 | 43.48 | 444.347 | 400.867 | 60.872 | 461.739 | 400.867 | 43.48 | 444.347 | 400.867 | 60.872 | 461.739 | 5.4476
2018 | 408.04 | 43.48 | 451.52 | 408.04 | 60.872 | 468.912 | 408.04 | 97.83 | 505.87 | 408.04 | 115.222 | 523.262 | 8.4403
2019 | 415.3884 | 43.48 | 458.8684 | 415.3884 | 60.872 | 476.2604 | 415.3884 | 97.83 | 513.2184 | 415.3884 | 115.222 | 530.6104 | 11.5061
2020 | 422.9165 | 43.48 | 466.3965 | 422.9165 | 60.872 | 483.7885 | 422.9165 | 97.83 | 520.7465 | 422.9165 | 115.222 | 538.1385 | 14.6469
2021 | 431.8123 | 43.48 | 475.2923 | 431.8123 | 60.872 | 492.6843 | 431.8123 | 97.83 | 529.6423 | 431.8123 | 115.222 | 547.0343 | 18.3583
2022 | 440.9591 | 43.48 | 484.4391 | 440.9591 | 43.48 | 484.4391 | 440.9591 | 97.83 | 538.7891 | 440.9591 | 97.83 | 538.7891 | 22.1744
2023 | 450.3639 |  | 450.3639 | 450.3639 |  | 450.3639 | 450.3639 | 54.35 | 504.7139 | 450.3639 | 54.35 | 504.7139 | 26.0982
2024 | 460.0338 |  | 460.0338 | 460.0338 |  | 460.0338 | 460.0338 | 54.35 | 514.3838 | 460.0338 | 54.35 | 514.3838 | 30.1326
2025 | 469.9765 |  | 469.9765 | 469.9765 |  | 469.9765 | 469.9765 | 26.9516 | 496.9282 | 469.9765 | 26.9516 | 496.9282 | 34.2808
2026 | 481.3344 |  | 481.3344 | 481.3344 |  | 481.3344 | 481.3344 |  | 481.3344 | 481.3344 |  | 481.3344 | 39.0194
2027 | 493.0481 |  | 493.0481 | 493.0481 |  | 493.0481 | 493.0481 |  | 493.0481 | 493.0481 |  | 493.0481 | 43.9065
2028 | 505.1289 |  | 505.1289 | 505.1289 |  | 505.1289 | 505.1289 |  | 505.1289 | 505.1289 |  | 505.1289 | 48.9467
2029 | 517.5882 |  | 517.5882 | 517.5882 |  | 517.5882 | 517.5882 |  | 517.5882 | 517.5882 |  | 517.5882 | 54.1448
2030 | 530.4379 |  | 530.4379 | 530.4379 |  | 530.4379 | 530.4379 |  | 530.4379 | 530.4379 |  | 530.4379 | 59.5059

## Figure C-1; Table C-2
Application for an Energy Project Certificate and An Energy Operation Certificate Regarding The Proposed Whitehorse Diesel-Natural Gas Conversion Project | [7 empty] | Yukon Energy Corporation UCG-YEC-1-2 Attachment 1 February 27, 2014
Figure C-1: Diesel Generation Requirements at Different Forecast Loads: 2013-2030
Application for an Energy Project Certificate and An Energy Operation Certificate Regarding The Proposed Whitehorse Diesel-Natural Gas Conversion Project | [5 empty] | Yukon Energy Corporation UCG-YEC-1-2 Attachment 1 February 27, 2014
Table C-2: Long-Term Average Diesel Generation at Different Forecast Loads: 2013-2030
Forecast Years | Base Case no Alexco |  | Base Case with Alexco |  | Scenario A1 - Base Case w Carmacks Copper (no Alexco) |  | Scenario A2 - Base Case w Carmacks Copper (with Alexco)
| Total Generation (GW.h) | Diesel (GW.h) | Total Generation (GW.h) | Diesel (GW.h) | Total Generation (GW.h) | Diesel (GW.h) | Total Generation (GW.h) | Diesel (GW.h)
2013 | 413.3991 | 11.1592 | 413.3991 | 11.1592 | 413.3991 | 11.1592 | 413.3991 | 11.1592
2014 | 415.9949 | 12.2577 | 415.9949 | 12.2577 | 415.9949 | 12.2577 | 415.9949 | 12.2577
2015 | 426.2799 | 16.9537 | 441.4979 | 25.7009 | 426.2799 | 16.9537 | 441.4979 | 25.7009
2016 | 437.3452 | 22.9 | 454.7372 | 33.1 | 437.3452 | 22.9 | 454.7372 | 33.1
2017 | 444.347 | 26.8728 | 461.739 | 37.6235 | 444.347 | 26.8728 | 461.739 | 37.6235
2018 | 451.52 | 31.3719 | 468.912 | 42.8161 | 505.87 | 68.9 | 523.262 | 81.8
2019 | 458.8684 | 36.117 | 476.2604 | 48.3197 | 513.2184 | 74.0791 | 530.6104 | 87.5764
2020 | 466.3965 | 41.1305 | 483.7885 | 54.0082 | 520.7465 | 80.0931 | 538.1385 | 94.1981
2021 | 475.2923 | 47.4275 | 492.6843 | 60.681 | 529.6423 | 87.5298 | 547.0343 | 102.1603
2022 | 484.4391 | 54.7414 | 484.4391 | 54.7414 | 538.7891 | 95.2347 | 538.7891 | 94.7808
2023 | 450.3639 | 33.0813 | 450.3639 | 33.0813 | 504.7139 | 69.8256 | 504.7139 | 69.8256
2024 | 460.0338 | 39.8099 | 460.0338 | 39.8099 | 514.3838 | 77.1854 | 514.3838 | 77.1854
2025 | 469.9765 | 46.8299 | 469.9765 | 46.8299 | 496.9282 | 71 | 496.9282 | 71
2026 | 481.3344 | 54.991 | 481.3344 | 54.991 | 481.3344 | 54.991 | 481.3344 | 54.991
2027 | 493.0481 | 63.5861 | 493.0481 | 63.5861 | 493.0481 | 63.5861 | 493.0481 | 63.5861
2028 | 505.1289 | 72.663 | 505.1289 | 72.663 | 505.1289 | 72.663 | 505.1289 | 72.663
2029 | 517.5882 | 82.276 | 517.5882 | 82.276 | 517.5882 | 82.276 | 517.5882 | 82.276
2030 | 530.4379 | 92.4873 | 530.4379 | 92.4873 | 530.4379 | 92.4873 | 530.4379 | 92.4873

## Table C-3; Figure C-2
| Application for an Energy Project Certificate and An Energy Operation Certificate Regarding The Proposed Whitehorse Diesel-Natural Gas Conversion Project | [7 empty] | Yukon Energy Corporation UCG-YEC-1-2 Attachment 1 February 27, 2014
Table C-3: Forecast Diesel Generation Variability (GW.h) Depending on Water Year Conditions - Load Scenarios for 2016/2018 and 31 Water Years of Record
|  | Average diesel generation required (GW.h) |  |  |  |  | Distribution of Annual Water Year Loads
| Water Year | 2016 Base Case no Alexco - load at 437.3 GW.h | 2016 Base Case w Alexco - load at 454.7 GW.h | Scenario A1 - 2018 load at 505.9 GW.h | Scenario A2 - 2018 load at 523.3 GW.h |  | % of Years not less than | 2016 Base Case no Alexco - load at 437.3 GW.h | 2016 Base Case w Alexco - load at 454.7 GW.h | Scenario A1 - 2018 load at 505.9 GW.h | Scenario A2 - 2018 load at 523.3 GW.h
| 1981 | 0.0816 | 4.1887 | 28.9298 | 41.1774 | 1 | 3.226% | 101.3985 | 109.9203 | 136.5252 | 148.7511
| 1982 | 1.6013 | 10.4082 | 68.1791 | 84.5625 | 2 | 6.452% | 76.0568 | 94.7076 | 134.9645 | 144.3449
| 1983 | 0.34055 | 22.2228 | 60.2153 | 73.304 | 3 | 9.677% | 68.8052 | 88.947 | 127.7181 | 140.5653
| 1984 | 5.9111 | 49.6178 | 88.8982 | 102.5043 | 4 | 12.9% | 63.0615 | 78.1441 | 112.3592 | 125.75
| 1985 | 24.3722 | 41.1208 | 75.7757 | 88.559 | 5 | 16.13% | 52.8466 | 66.7569 | 110.5128 | 124.7615
| 1986 | 46.1719 | 40.4291 | 73.112 | 86.0124 | 6 | 19.35% | 52.0917 | 55.4286 | 88.8982 | 105.4832
| 1987 | 11.6755 | 16.9322 | 51.6334 | 65.0316 | 7 | 22.58% | 46.1719 | 49.6178 | 88.7278 | 103.4374
| 1988 | 15.2059 | 24.4564 | 52.2171 | 64.5075 | 8 | 25.81% | 35.5666 | 48.2919 | 80.6599 | 102.5043
| 1989 | 2.3195 | 7.2007 | 31.6217 | 44.0684 | 9 | 29.03% | 26.2908 | 41.1208 | 78.1999 | 91.657
| 1990 | 1.0693 | 12.8674 | 52.0638 | 65.871 | 10 | 32.26% | 24.3722 | 40.4291 | 77.4109 | 90.4756
| 1991 | 0.31455 | 2.8981 | 37.4195 | 51.5004 | 11 | 35.48% | 23.0826 | 37.3494 | 76.7629 | 89.216
| 1992 | 0.0726 | 0.1637 | 14.4815 | 23.7239 | 12 | 38.71% | 19.055 | 36.2127 | 75.8323 | 88.559
| 1993 | 0.6423 | 1.3238 | 28.5611 | 40.8583 | 13 | 41.94% | 17.4106 | 29.393 | 75.7757 | 87.4646
| 1994 | 0.0726 | 3.6626 | 80.6599 | 103.4374 | 14 | 45.16% | 16.9942 | 27.1479 | 73.112 | 86.0124
| 1995 | 35.5666 | 78.1441 | 127.7181 | 140.5653 | 15 | 48.39% | 15.2562 | 26.6995 | 71.4168 | 84.5625
| 1996 | 63.0615 | 94.7076 | 134.9645 | 148.7511 | 16 | 51.61% | 15.2059 | 25.943 | 68.1791 | 82.612
| 1997 | 68.8052 | 88.947 | 112.3592 | 124.7615 | 17 | 54.84% | 15.0384 | 25.3927 | 60.9253 | 74.6062
| 1998 | 76.0568 | 66.7569 | 110.5128 | 125.75 | 18 | 58.06% | 11.6755 | 24.4564 | 60.6137 | 73.5344
| 1999 | 101.3985 | 109.9203 | 136.5252 | 144.3449 | 19 | 61.29% | 8.4629 | 22.2228 | 60.3549 | 73.304
| 2000 | 52.8466 | 48.2919 | 76.7629 | 89.216 | 20 | 64.52% | 7.3298 | 18.8597 | 60.2153 | 69.5095
| 2001 | 23.0826 | 16.0002 | 37.2378 | 46.2294 | 21 | 67.74% | 5.9111 | 16.9322 | 52.7384 | 65.871
| 2002 | 26.2908 | 27.1479 | 52.7384 | 65.7904 | 22 | 70.97% | 2.3195 | 16.0002 | 52.2171 | 65.7904
| 2003 | 15.0384 | 29.393 | 75.8323 | 87.4646 | 23 | 74.19% | 1.6013 | 12.8674 | 52.0638 | 65.0316
| 2004 | 52.0917 | 55.4286 | 88.7278 | 105.4832 | 24 | 77.42% | 1.0693 | 10.4082 | 51.6334 | 64.5075
| 2005 | 19.055 | 25.943 | 77.4109 | 90.4756 | 25 | 80.65% | 0.99662 | 7.2007 | 37.4195 | 51.5004
| 2006 | 15.2562 | 37.3494 | 78.1999 | 91.657 | 26 | 83.87% | 0.6423 | 4.1887 | 37.2378 | 46.2294
| 2007 | 16.9942 | 36.2127 | 60.6137 | 73.5344 | 27 | 87.1% | 0.34055 | 3.8556 | 31.6217 | 44.0684
| 2008 | 17.4106 | 25.3927 | 60.3549 | 69.5095 | 28 | 90.32% | 0.31455 | 3.6626 | 28.9298 | 41.1774
| 2009 | 0.99662 | 3.8556 | 28.5556 | 40.516 | 29 | 93.55% | 0.0816 | 2.8981 | 28.5611 | 40.8583
| 2010 | 8.4629 | 18.8597 | 60.9253 | 74.6062 | 30 | 96.77% | 0.0726 | 1.3238 | 28.5556 | 40.516
| 2011 | 7.3298 | 26.6995 | 71.4168 | 82.612 | 31 | 100% | 0.0726 | 0.1637 | 14.4815 | 23.7239
| Average | 22.8902 | 33.1143 | 68.8588 | 81.8189 |  |  | 22.8902 | 33.1143 | 68.8588 | 81.8189
| Application for an Energy Project Certificate and An Energy Operation Certificate Regarding The Proposed Whitehorse Diesel-Natural Gas Conversion Project | [7 empty] | Yukon Enery Corporation UCG-YEC-1-2 Attachment 1 February 27, 2014
Figure C-2: Duration Curve – Required Diesel Generation Hydro Grid Annual Water Variability

## Table C-4
Application for an Energy Project Certificate and An Energy Operation Certificate Regarding The Proposed Whitehorse Diesel-Natural Gas Conversion Project | [9 empty] | Yukon Energy Corporation UCG-YEC-1-2 Attachment 1 February 27, 2014
Table C-4: Grid Capacity Planning - Forecast MW Surplus (Shortfall) by Load Scenario: 2013-2030
Forecast Years | Base Case no Alexco |  |  | Base Case with Alexco |  |  | Scenario A1 - Base Case w Carmacks Copper (no Alexco) |  |  | Scenario A2 - Base Case w Carmacks Copper (with Alexco)
| Peak MW | N-1 Surplus (shortfall) (MW) | LOLE Surplus (shortfall) (MW) | Peak MW | N-1 Surplus (shortfall) (MW) | LOLE Surplus (shortfall) (MW) | Peak MW | N-1 Surplus (shortfall) (MW) | LOLE Surplus (shortfall) (MW) | Peak MW | N-1 Surplus (shortfall) (MW) | LOLE Surplus (shortfall) (MW)
2013 | 81.04 | 4.645 | 4.645 | 73.84 | 4.645 | 4.645 | 73.84 | 4.645 | 4.645 | 73.84 | 4.645 | 4.645
2014 | 80.6324 | -0.84744 | -0.84744 | 80.6324 | -0.84744 | -0.84744 | 80.6324 | -0.84744 | -0.84744 | 80.6324 | -0.84744 | -0.84744
2015 | 82.7598 | -6.9748 | -6.9748 | 85.4348 | -6.9748 | -6.9748 | 82.7598 | -6.9748 | -6.9748 | 85.4348 | -6.9748 | -6.9748
2016 | 84.3257 | -8.5407 | -8.5407 | 87.0007 | -8.5407 | -8.5407 | 84.3257 | -8.5407 | -8.5407 | 87.0007 | -8.5407 | -8.5407
2017 | 85.7306 | -10.8656 | -10.8656 | 88.4056 | -10.8656 | -10.8656 | 85.7306 | -10.8656 | -10.8656 | 88.4056 | -10.8656 | -10.8656
2018 | 87.1698 | -13.0248 | -13.0248 | 89.8448 | -13.0248 | -13.0248 | 94.4483 | -13.0248 | -13.0248 | 97.1233 | -13.0248 | -15.2783
2019 | 88.6442 | -17.0492 | -17.0492 | 91.3192 | -17.0492 | -17.0492 | 95.9227 | -17.0492 | -17.0492 | 98.5977 | -17.0492 | -19.3027
2020 | 90.1546 | -20.6796 | -20.6796 | 92.8296 | -20.6796 | -20.6796 | 97.4331 | -20.6796 | -20.6796 | 100.1081 | -20.6796 | -22.9331
2021 | 91.9395 | -30.9645 | -30.9645 | 94.6145 | -30.9645 | -30.9645 | 99.218 | -30.9645 | -30.9645 | 101.893 | -30.9645 | -33.218
2022 | 93.7747 | -32.7997 | -32.7997 | 93.7747 | -32.7997 | -32.7997 | 101.0532 | -32.7997 | -32.7997 | 101.0532 | -32.7997 | -32.7997
2023 | 90.3617 | -34.6867 | -34.6867 | 90.3617 | -34.6867 | -34.6867 | 97.6402 | -34.6867 | -34.6867 | 97.6402 | -34.6867 | -34.6867
2024 | 92.3019 | -36.6269 | -36.6269 | 92.3019 | -36.6269 | -36.6269 | 99.5804 | -36.6269 | -36.6269 | 99.5804 | -36.6269 | -36.6269
2025 | 94.2968 | -45.6218 | -45.6218 | 94.2968 | -45.6218 | -45.6218 | 101.5753 | -45.6218 | -45.6218 | 101.5753 | -45.6218 | -45.6218
2026 | 96.5757 | -50.9007 | -50.9007 | 96.5757 | -50.9007 | -50.9007 | 96.5757 | -50.9007 | -50.9007 | 96.5757 | -50.9007 | -50.9007
2027 | 98.9259 | -56.0509 | -56.0509 | 98.9259 | -56.0509 | -56.0509 | 98.9259 | -56.0509 | -56.0509 | 98.9259 | -56.0509 | -56.0509
2028 | 101.3498 | -58.4748 | -58.4748 | 101.3498 | -58.4748 | -58.4748 | 101.3498 | -58.4748 | -58.4748 | 101.3498 | -58.4748 | -58.4748
2029 | 103.8497 | -60.9747 | -60.9747 | 103.8497 | -60.9747 | -60.9747 | 103.8497 | -60.9747 | -60.9747 | 103.8497 | -60.9747 | -60.9747
2030 | 106.4279 | -63.5529 | -63.5529 | 106.4279 | -63.5529 | -63.5529 | 106.4279 | -63.5529 | -63.5529 | 106.4279 | -63.5529 | -63.5529
Notes:
1. Non-industrial peak numbers for 2014-2030 are calculated based on YEC’s three year average non-industrial load factor (2011-2013).
2. Minto at 4.8 MW in 2014, increasing to 5.3 in 2015 and shut-down in 2022; the cases with Alexco assume 2.7 MW load for 2015-2021; Carmacks Copper assumed at 7.3 MW.
3. Yukon Grid installed winter firm capacity at 114.49 MW by end of 2013 excluding Fish Lake Hydro and Haines Junction diesel. Total retirements are at 35.6 MW over 2014-2030.
4. The N-1 event assumes loss of the Aishihik transmission line, i.e., all generation capacity at Aishihik (37 MW) and at Haines Junction (1.75 MW) is assumed not to be available to meet grid peak load excluding Haines Junction load (approximately 1 MW).

## Table D-1
Application for an Energy Project Certificate and An Energy Operation Certificate Regarding The Proposed Whitehorse Diesel-Natural Gas Conversion Project | [13 empty] | Yukon Energy Corporation UCG-YEC-1-2 Attachment 1 February 27, 2014
Table D-1: Diesel Displacement Benefits of LNG Plant – Load for 2015, Base Case no Alexco
LNG Plant (Capacity Factor=0.91) | LNG Year Round Operation - Base Case | [5 empty] | Drought Water Years Diesel Generation (GW.h/yr) | [8 empty] | # of yrs with Diesel Gen-n Greater than 5 GW.h
| Energy (GW.h/yr) |  |  | Remaining LTA Diesel Generation | Incremental Diesel Reduction (%) | Total Diesel Reduction (%) | Highest Annual Diesel |  | Drought Water year sequence (averaged by WY) |  |  |  |  | Highest Weekly Diesel
| Total | Displacing Diesel | Displacing Hydro |  |  |  | Before Averaging | After Averaging | 1995 | 1996 | 1997 | 1998 | 1999 | GW.h/ week | MW
| A=B+C | B | C | D=17.2-B | E=chD/chA | F=B/17.2 | G | H=Max(I-M) | I | J | K | L | M | N | O=N/168*1000 | P (out of 31)
W/o LNG Plant |  |  |  | 17.2146 |  |  | 110.8 | 106.284 | 15.0345 | 58.0283 | 59.5111 | 40.7288 | 106.284 | 5.9712 | 35.5429 | 16
1 MW LNG Plant | 7.9716 | 3.069 | 4.9026 | 14.1457 | 38.5% | 17.83% | 105.4 | 101.8161 | 3.7357 | 53.4266 | 54.284 | 34.9476 | 101.8161 | 5.7156 | 34.0214 | 13
|  | 38.5% | 61.5%
2 MW LNG Plant | 15.9432 | 5.4854 | 10.4578 | 11.7293 | 30.31% | 31.86% | 100.1 | 96.9827 | 0.0037 | 42.6464 | 49.1984 | 23.1112 | 96.9827 | 5.565 | 33.125 | 13
|  | 34.41% | 65.59%
3 MW LNG Plant | 23.9148 | 8.2883 | 15.6265 | 8.9263 | 35.16% | 48.15% | 94.8 | 85.4369 | 0.0011 | 28.3275 | 44.0701 | 14.2095 | 85.4369 | 5.4278 | 32.3083 | 8
|  | 34.66% | 65.34%
4 MW LNG Plant | 31.8864 | 10.8754 | 21.011 | 6.3392 | 32.45% | 63.18% | 89.9 | 71.682 | 0 | 14.2294 | 39.124 | 7.9692 | 71.682 | 5.2195 | 31.0685 | 8
|  | 34.11% | 65.89%
5 MW LNG Plant | 39.858 | 12.8811 | 26.9769 | 4.3335 | 25.16% | 74.83% | 71.9 | 66.0465 | 0 | 0.4892 | 34.5553 | 1.7126 | 66.0465 | 5.0706 | 30.1821 | 5
|  | 32.32% | 67.68%
6 MW LNG Plant | 47.8296 | 14.6335 | 33.1961 | 2.5811 | 21.98% | 85.01% | 72.4 | 57.7082 | 0 | 0.0054 | 16.7958 | 0.2565 | 57.7082 | 4.4393 | 26.4244 | 3
|  | 30.6% | 69.4%
7 MW LNG Plant | 55.8012 | 15.7087 | 40.0925 | 1.506 | 13.49% | 91.25% | 45.6 | 45.5677 | 0 | 0 | 0.004 | 0.1885 | 45.5677 | 4.2824 | 25.4905 | 1
|  | 28.15% | 71.85%
8 MW LNG Plant | 63.7728 | 16.6211 | 47.1517 | 0.59355 | 11.45% | 96.55% | 18.3 | 18.2666 | 0 | 0 | 0 | 0.1304 | 18.2666 | 3.5055 | 20.8661 | 1
|  | 26.06% | 73.94%
9 MW LNG Plant | 71.7444 | 17.2114 | 54.533 | 0.0032258 | 7.405% | 99.98% | 0.1 | 0.0784 | 0 | 0 | 0 | 0.0784 | 0.0055 | 0.0784 | 0.46667 | 0
|  | 23.99% | 76.01%
Notes:
1. LNG plant assumed with year round operation at 97% capacity factor in winter months (weeks 1-20, 46-52) and 84.5% capacity factor in summer months (weeks 21-45), annual average capacity factor is 91%.
2. Numbers are based on YECSIM model version with updates (water years, Mayo Lake outlet channel rating curve, Aishihik rolling average). Assumes no Mayo Lake license change impact and no other new renewable generations.
3. Numbers in column D are long-term averages (average of 31 water years [1981-2011] and 13 load years).
4. Numbers in column G are highest annual diesel generation out of 403 data points (31 water years and 13 load years).
5. Numbers in columns I-M are averaged annual diesel generations by load years.
6. Numbers in column N are highest weekly diesel generation (highest out of 20,956 data points = 31 water years, 13 load years and 52 weeks).
7. Numbers in column O are calculated based on numbers in column N divided by 168 hrs in a week.
8. The load forecast is based on November 30, 2013 update. Load shape for the run is based on 2014 BP non-industrial plus industrial load.

## Table D-2
Application for an Energy Project Certificate and An Energy Operation Certificate Regarding The Proposed Whitehorse Diesel-Natural Gas Conversion Project | [13 empty] | Yukon Energy Corporation UCG-YEC-1-2 Attachment 1 February 27, 2014
Table D-2: Diesel Displacement Benefits of LNG Plant – Load for 2016 and 2017, Base Case no Alexco
LNG Plant (Capacity Factor=0.91) | LNG Year Round Operation - Base Case | [5 empty] | Drought Water Years Diesel Generation (GW.h/yr) | [8 empty] | # of yrs with Diesel Gen-n Greater than 5 GW.h
| Energy (GW.h/yr) |  |  | Remaining LTA Diesel Generation | Incremental Diesel Reduction (%) | Total Diesel Reduction (%) | Highest Annual Diesel |  | Drought Water year sequence (averaged by WY) |  |  |  |  | Highest Weekly Diesel
| Total | Displacing Diesel | Displacing Hydro |  |  |  | Before Averaging | After Averaging | 1995 | 1996 | 1997 | 1998 | 1999 | GW.h/ week | MW
| A=B+C | B | C | D=Diesel-B | E=chD/chA | F=B/Diesel | G | H=Max(I-M) | I | J | K | L | M | N | O=N/168*1000 | P (out of 31)
Load at 437.3 GW.h/2016
W/o LNG Plant |  |  |  | 22.8993 |  |  | 119.2 | 101.3985 | 35.5666 | 63.0615 | 68.8052 | 76.0568 | 101.3985 | 6.2565 | 37.2411 | 21
7 MW LNG Plant | 55.8012 | 19.6161 | 36.1851 | 3.2831 | 35.15% | 85.66% | 75.4 | 62.0714 | 0 | 0.0084 | 25.308 | 0.2974 | 62.0714 | 4.5029 | 26.803 | 4
|  | 35.15% | 64.85%
8 MW LNG Plant | 63.7728 | 20.9141 | 42.8587 | 1.9851 | 16.28% | 91.33% | 54.3 | 51.343 | 0 | 0.0016 | 7.3177 | 0.2235 | 51.343 | 4.3462 | 25.8702 | 2
|  | 32.79% | 67.21%
9 MW LNG Plant | 71.7444 | 21.8896 | 49.8548 | 1.0097 | 12.24% | 95.59% | 31.1 | 31.1447 | 0 | 0 | 0.002 | 0.1767 | 31.1447 | 4.1822 | 24.894 | 1
|  | 30.51% | 69.49%
10 MW LNG Plant | 79.716 | 22.7638 | 56.9522 | 0.13548 | 10.97% | 99.41% | 4.1 | 4.0732 | 0 | 0 | 0 | 0.1199 | 4.0732 | 2.2435 | 13.3542 | 0
|  | 28.56% | 71.44%
11 MW LNG Plant | 87.6876 | 22.896 | 64.7916 | 0.0032258 | 1.659% | 99.99% | 0.1 | 0.0794 | 0 | 0 | 0 | 0.0794 | 0.0023 | 0.0794 | 0.47262 | 0
|  | 26.11% | 73.89%
Load at 444.3 GW.h/2017
W/o LNG Plant |  |  |  | 26.9752 |  |  | 124 | 103.7673 | 52.6754 | 76.8202 | 81.6284 | 72.3448 | 103.7673 | 6.4381 | 38.322 | 21
7 MW LNG Plant | 55.8012 | 21.8392 | 33.962 | 5.136 | 39.14% | 80.96% | 86.8 | 68.2387 | 0 | 6.2239 | 36.3982 | 5.0653 | 68.2387 | 5.2086 | 31.0036 | 8
|  | 39.14% | 60.86%
8 MW LNG Plant | 63.7728 | 23.7931 | 39.9797 | 3.1821 | 24.51% | 88.2% | 76.4 | 61.4622 | 0 | 0.0065 | 24.3146 | 0.305 | 61.4622 | 4.4902 | 26.7274 | 4
|  | 37.31% | 62.69%
9 MW LNG Plant | 71.7444 | 25.0521 | 46.6923 | 1.9231 | 15.79% | 92.87% | 52.5 | 50.5504 | 0 | 0.0011 | 6.4322 | 0.2364 | 50.5504 | 4.3262 | 25.7512 | 2
|  | 34.92% | 65.08%
10 MW LNG Plant | 79.716 | 26.0236 | 53.6924 | 0.95161 | 12.19% | 96.47% | 29.3 | 29.2642 | 0 | 0 | 0.002 | 0.1725 | 29.2642 | 4.1622 | 24.775 | 1
|  | 32.65% | 67.35%
11 MW LNG Plant | 87.6876 | 26.8945 | 60.7931 | 0.080645 | 10.93% | 99.7% | 2.4 | 2.3857 | 0 | 0 | 0 | 0.1324 | 2.3857 | 1.7646 | 10.5036 | 0
|  | 30.67% | 69.33%
12 MW LNG Plant | 95.6592 | 26.972 | 68.6872 | 0.0032258 | 0.9712% | 99.99% | 0.1 | 0.0844 | 0 | 0 | 0 | 0.0844 | 0.0017 | 0.0844 | 0.50238 | 0
|  | 28.2% | 71.8%
Notes:
1. LNG plant assumed with year round operation at 97% capacity factor in winter months (weeks 1-20, 46-52) and 84.5% capacity factor in summer months (weeks 21-45), annual average capacity factor is 91%.
2. Numbers are based on YECSIM model version with updates (water years, Mayo Lake outlet channel rating curve, Aishihik rolling average). Assumes no Mayo Lake license change impact and no other new renewable generations.
3. Numbers in column D are long-term averages (average of 31 water years [1981-2011] and 13 load years).
4. Numbers in column G are highest annual diesel generation out of 403 data points (31 water years and 13 load years).
5. Numbers in columns I-M are averaged annual diesel generations by load years.
6. Numbers in column N are highest weekly diesel generation (highest out of 20,956 data points = 31 water years, 13 load years and 52 weeks).
7. Numbers in column O are calculated based on numbers in column N divided by 168 hrs in a week.
8. The load forecast is based on November 30, 2013 update. Load shape for the run is based on 2014 BP non-industrial plus industrial load.